## Sheet1
| Particle count readings with Dust Trax |  |  |  |  | Gauge Reading
Absolent |  | After 1st | After 2nd | After | 1st | 2nd | HEPA
Serial Number | Inlet | Filter | Filter | HEPA | Bottom | Middle | Top | Notes
20080205 | 1.7 | 0.12 | 0.135 | 0.124 | 100 | 0 | 0 | No Filter in the 2nd
ODR 3000 | [7 empty] | and HEPA stages
2 machines
20070652 | 13.2 | 0.605 | 0.12 | 0.17 | 1900 | 100 | 250 | 1st stage needs to be
ODR 3000 |  |  |  | HEPA had expanded metal sitting in it |  |  |  | chnaged.
4 machines
20070651 | 33 | 38 | 37 | 27 | 100 | In Orange | 175 | 2nd stage needs to be
ODR 3000 | [7 empty] | changed
6 machines
20070649 | 31 | 0.08 | 0.011 | 0.006 | 3500 | 100 | 100 | 1st stage needs to be
ODR 3000 | [7 empty] | changed
4 machines
20060457 | 41.7 | 2.95 | 1.09 | 0.01 | 1700 | 0 | 2100 | Middle gauges are bad
ODR 9000 | 30.1 | 1.03 | 1.65 | 0.01 | 1200 | 0 | 400 | All HEPAs need to be
7 machines | 30.1 | 1.39 | 1.17 | 0.008 | 800 | 5 | 2400 | changed
Sheldons Fan
20HP s/n 09P0114583G-1
20080207 | 40 | 5.5 | 1.63 | 0.558 | 400 | 200 | 1200 | HEPA needs to be
ODR 2000 | [7 empty] | changed
7 machines
20070650 | 42.7 | 3.74 | 1.2 | 0.017 | 450 | 250 | 800 | HEPA needs to be
ODR 3000 | [7 empty] | changed
9 machines
20071254 | 1.67 | 0.071 | 0.014 | 0.01 | 150 | 100 | 100
ODF 2000
1 machine
20080206 | 8.05 | 4.53 | 4.5 | 1.39 | 300 | 200 | 250 | 1st stage not filtering?
ODR 3000 |  | connected to oil container / need to be routed to work area
3 machines
20001131 | Gauges not reading / all filters need to be changed
ODF 800
F-755 / 2 drops
20001728 | No readings / Not running
washing machine
20050903 | No readings / Not running
ODF 800
Bryant