Alcoa – San Antonio Works

14555 Old Corpus Christi Road

Elmendorf, TX 78112

8/25/2015

Case # 1473

- Inspected SDC-20-12 Type 1 Dust Collector.

  - Inside was very clean with very little dust inside

  - Remove several filter to check for filter bypass. There was no evidence of any bypass. Area above filters was very clean.

- Opened all dust collection draws in system and found no dust collected.

- Took flow reading in each duct run as follows:

  - In duct from Downdraft Table with damper from Booth closed.

  - In duct from Booth with damper from Downdraft Table closed.

- Flow valves were as follows:

  - From Table:

| Location # | Table Duct |  |  |
| --- | --- | --- | --- |
| Data Point | VP | V | CFM |
| 1 | 0.750 | 3468 | 4047 |
| 2 | 0.600 | 3102 | 3619 |
| 3 | 0.590 | 3076 | 3589 |
| 4 | 0.700 | 3351 | 3909 |
| 5 | 0.820 | 3627 | 4231 |
| 6 | 0.750 | 3468 | 4047 |
| 7 | 1.000 | 4005 | 4673 |
| 8 | 1.100 | 4200 | 4901 |
| 9 | 0.810 | 3605 | 4205 |
| Average | 0.791 | 3562 | 4156 |
| Duct Area: | 1.17 |  |  |
| Length | Width | Area SF |  |
| 12.00 | 14.00 | 1.17 |  |

  - Static pressure was 8.5”WC

  - From Booth:

| Location # | Booth Duct |  |  |
| --- | --- | --- | --- |
| Data Point | VP | V | CFM |
| 1 | 1.23 | 4442 | 5182 |
| 2 | 1.34 | 4636 | 5409 |
| 3 | 1.11 | 4220 | 4923 |
| 4 | 1.34 | 4636 | 5409 |
| 5 | 1.55 | 4986 | 5817 |
| 6 | 1.23 | 4442 | 5182 |
| 7 | 1.33 | 4619 | 5389 |
| 8 | 0.90 | 3799 | 4433 |
| 9 | 0.87 | 3736 | 4358 |
| Average | 1.21 | 4408 | 5142 |
| Duct Area: | 1.17 |  |  |
| Length | Width | Area SF |  |
| 12.00 | 14.00 | 1.17 |  |

  - Static pressure was 5.0”WC

  - Static pressure with both open was as follows:

    - Table duct: 3.3”WC

    - Booth duct: 2.8”WC

- Downdraft Table

  - Took surface air velocity reading data as follows:

| Downdraft Table Reading |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Point # | Reading (FPM) | Test Point # | Reading (FPM) | Test Point # | Reading (FPM) | Test Point # | Reading (FPM) |
| TP 1 | 900 | TP 5 | 910 | TP 9 | 681 | TP 13 | 625 |
| TP 2 | 916 | TP 6 | 858 | TP 10 | 681 | TP 14 | 681 |
| TP 3 | 604 | TP 7 | 818 | TP 11 | 564 | TP 15 | 506 |
| TP 4 | 584 | TP 8 | 623 | TP 12 | 400 | TP 16 | 409 |

  - Readings went to zero within 4 to 5 inch above the surface of the table.

- Booth

  - The booth was setup as follows:

    - Left Section front had only the bottom slot (one of four) open.

    - Left Section top had only the rear most slot (nearest the opening)(one of two) open.

    - Right Section front had the two bottom slots open.

    - Right Section top had both slots open.

  - Air velocity reading at the slots were as follows:

    - Left front bottom slot – 2600FPM

    - Left Top Slot – 2850FPM

    - Right Section front bottom slot – 1250FPM

    - Right Section front next slot up – 1265FPM

    - Right Section top rear – 1350FPM

    - Right Section top front – 1230FPM

  - All readings went to zero within 3 inch from the slots.

  - I could not measure any air flow across the work table in the booth.

The collector is rated at 8000CFM.  Opening more of the slots in the booth may help.  We should be able to get approximately 3000 more CFM in the booth.  The downdraft table ducting is only allowing about 50% air flow.

Bill Boisvert

Bill Boisvert, Project Specialist

Cell: 919-971-3910 - Office: 919-488-5195

E-mail: bboisvert@avanienvironmental.com